Section 26 33 23

Three Phase Centralized Emergency Lighting Inverter

- Guide Specification for 10KW – 33KW Systems

- (Optional Items in Red)

PART 1 - GENERAL

1.1	Description

This specification defines the electrical and mechanical characteristics and requirements for a three phase uninterruptible stored emergency power supply system. The system as specified herein includes all the components required to deliver reliable, high quality uninterruptible power for emergency illumination and related life safety equipment. The system shall incorporate an online, dual conversion, microprocessor DSP controlled, high frequency, IGBT PWM input PFC converter and output inverter, a high speed automatic bypass transfer device, a battery charger, an energy storage battery platform, an advanced full diagnostic monitor with automatic system testing and a touchscreen color LCD display panel, as well as all the related hardware components and software to facilitate a functional centralized system. The emergency power supply system shall provide immunity from power line disturbances and power interruptions. The specified system shall include an uninterrupted, normally on output power section and a normally off standby output power section, thus enabling compatibility with emergency lighting fixtures operating in (a) normally on and standby mode(s). A self-diagnostic monitoring alarm system shall continuously advise of system status and battery condition.

- 1.2	Standards

The system shall be designed in accordance with applicable portions of the following standards:

- American National Standards Institute (ANSI C57.110)

- American National Standards Institute (ANSI C62.41 Category B-3)

- Institute of Electrical and Electronic Engineers (IEEE 519-1992)

- National Electrical Manufacturers Association (NEMA PE 1-2003)

- National Electric Code (Latest Revision of NEC Article 700 – Emergency Systems)

- National Fire Protection Association (NFPA 70) (NFPA 101) (NFPA 111) (NFPA 99)

- NFPA 101 Section 7.9.3.1.3 – Periodic Testing of Emergency Lighting Equipment

- Federal Communications Commission (FCC Class A limits, 47 C.F.R. Part 15, Subparts A, B)

- Listed UL Standard: ANSI/UL 924 Emergency Lighting and Power Equipment rated with 90 minutes of battery backup time, for use in accordance with NEC Article 700 (ANSI/NFPA 70), the Life Safety Code (ANSI/NFPA 101), and the International Building Code (IBC).

Or specify:

(UL 924 Auxiliary Lighting and Power Equipment for other than 90 minutes of battery backup time, for use in conjunction with a facility emergency lighting and power system.)

(C-UL listed to CSA C22.2, No. 141-15, Emergency Lighting Equipment with 30 minutes of battery backup time.)  Engineer’s Note: Consult factory for other C-UL listed battery run times.

Inverter systems shall be seismic-rated and tested in accordance with applicable portions of the following additional standards:

- ICC - AC156: “Acceptance Criteria for Seismic Certification by Shake-Table Testing of  Nonstructural Components and Systems”

- ASCE 7-10

- California Building Code – CBC 2016

- International Building Code – IBC 2015

  - Submittals

A.          Manufacturer Requirements:

- The manufacturer shall be ISO 9001:2015 “Quality Assurance Certified” and shall upon request furnish certification documents.

- The manufacturer shall be a United States based manufacturer with 15 years experience or greater in design and fabrication of centralized stored electrical energy emergency and standby power systems.

B.          Product Data:

- The manufacturer shall supply documentation for the installation of the system, including wiring diagrams and cabinet outlines showing dimensions, weights, BTUs, input/output current, input/output connection locations and required clearances.

- Factory test results shall be provided to show compliance with the requirements. The manufacturer shall include battery test documentation which demonstrates compliance with the specified minimum emergency reserve with full rated KW load.

- The supplier shall furnish (6) equipment submittal copies. Submittals shall be specific for the equipment furnished and shall include as-built information.

- The manufacturer shall supply a seismic testing certificate of compliance to validate that the system was shake-table tested and met the code requirements specified.

PART 2 - PRODUCTS

- 2.1	Manufacturers

The equipment specified shall be the EON Model EL3 centralized emergency lighting inverter system, manufactured by Trystar.

2.2         Manufactured Units

    - The system shall be designed and manufactured to assure maximum reliability, serviceability and performance. All control devices and system electronics shall be accessible via the front of the inverter cabinet for rapid service or replacement. The system’s advanced monitor shall be mounted on the front door of the inverter cabinet for easy observation of system status, electrical measurements and battery condition. The system is to be furnished with an internally located inverter input circuit breaker, inverter output circuit breaker, and bypass switch. System batteries shall be provided in a separate standalone front access battery cabinet, matching the height and depth of the inverter cabinet. The batteries and DC conductors shall be DC circuit breaker protected. Cabinets are to be floor mounted, constructed of steel, powder-coated, and NEMA 1 rated for indoor use, and provided with a field installed drip shield. The inverter controls, bypass, and breakers shall be front accessible through a hinged, key lockable door. The inverter cabinet shall have a protective dead front panel that allows the operation of the bypass switch and AC breakers while preventing physical contact with live electrical connections. All conductors and transformer windings shall be copper constructed. Seismic-rated systems shall be provided with floor mounting brackets.

    - The system shall include a factory-installed, side-mounted, 14” wide output distribution cabinet designed for front access only service. Located within the distribution cabinet shall be (factory-installed output branch circuit breakers as specified in Section 2.16 of this specification) (and) (the standby, normally off AC output bus as specified in Sections 2.3 C of this specification). The output distribution cabinet shall be capable of accommodating 1 pole, 2 pole, and 3 pole branch circuit breakers fed from the inverter system output of (208/120 VAC) (480/277 VAC). A total of (12 pole positions per phase shall be available for unmonitored breakers) (8 pole positions per phase shall be available for monitored breakers). Circuit breakers shall be wired to the (normally on AC output bus) (and) (normally off AC output bus) as specified in Section 2.16. The output distribution cabinet shall include a hinged, key lockable front door.

    - The system shall operate in accordance with requirements as specified herein to support any combination of  LED lighting, fluorescent ballast fixtures, incandescent lamps, electronic and high power factor fluorescent ballasts, quartz re-strike HID fixtures, halogen, or other approved loads up to the output rating of the system. The “Normally On” and “Normally Off” AC output(s) shall be 100% rated and limited only by the system’s maximum KVA/KW output rating.

2.3         Modes of Operation

    - Normal Operation: The load is supplied with regulated power derived from the normal AC power input terminals through the input PFC AC/DC converter and output DC/AC inverter. A full load rated DC/DC battery charger shall be used to charge the batteries.

    - Uninterrupted Emergency Operation: Upon the failure or unacceptable deviation of commercial AC power, energy shall be supplied by the battery through the output DC/AC inverter and shall continue to supply power to the load without switching loss or disturbance. When power is restored at the AC input terminals of the system, the input AC/DC PFC converter shall supply power to the load through the output DC/AC inverter. Simultaneously the DC/DC battery charger shall recharge the batteries. There shall be no break or interruption of power to the load upon failure or restoration of the commercial AC power.

    - Standby Emergency Operation: Upon the failure or unacceptable deviation of commercial AC power, or upon a remote input “command on signal”, the standby, normally off AC output bus shall become energized, thus providing emergency power for standby lighting fixtures which are required to illuminate only in the event of emergency. User-adjustable settings shall be programmable via the touch screen LCD display panel and include transfer on delay time (0 to 8 seconds), transfer off delay time (0 to 15 minutes), and a soft start control (0 to 172 cycles) to accommodate the high inrush current associated with energizing normally off emergency lights.

    - Automatic Restart: If the loss of AC input power exceeds the available battery run time, a low battery shutdown shall occur to protect the batteries. Once the AC input power source returns and is within acceptable voltage and frequency limits, the inverter system shall (automatically restart)(require a manual restart).

    - Manual Restart: The inverter system shall require a manual restart from a shutdown resulting from the following events.

- Remote or local emergency power off activated

- Inverter system failure

- Low battery shutdown, if manual restart option is selected

2.4         Automatic Bypass Operation

    - Automatic Bypass: The system shall include an automatic static bypass for fault clearing, instantaneous overload conditions that exceed specified levels and/or to connect the load to the AC input power bypass source in the event of a system fault or failure. The static bypass switch shall transfer the load from the inverter output to the AC input power bypass source under the following fault conditions.

- Output overload capacity exceeded

- Inverter output voltage or frequency out of limits

- Inverter system failure

- Over temperature

- DC bus out of limits

- Manual bypass switch transfer initiated

    - Automatic Bypass Inhibited: The static bypass switch shall not transfer the load from the inverter output to the AC input power bypass source if that source is not within limits when a fault condition occurs. If the AC input power bypass source is out of limits (factory set at +8, -12% of nominal voltage and +/-5% of nominal frequency), the inverter system shall shut down and an alarm shall sound.

    - Automatic Retransfer from Bypass: The retransfer of the load from the AC input power bypass source to the inverter output shall be automatically initiated whenever the inverter is capable of assuming the critical load.

    - Automatic Retransfer Inhibited: The retransfer of the load from the AC input power bypass source to the inverter output shall be inhibited if any of the following conditions exist.

- Inverter output not in sync range with AC input power source

- Voltage difference between inverter output and AC input power bypass source exceeds limits

- Inverter system failure

- System in static bypass resulting from an over temperature condition

2.5         Manual Bypass Operation

    - Internal Bypass Switch: The inverter system shall include a standard push-to-turn, make-before-break bypass switch, accessible behind the front door of the inverter enclosure. Pushing the manual bypass switch shall invoke the inverter’s static bypass prior to turning the switch to the bypass position. The bypass switch shall provide complete isolation of the inverter output terminals from external circuits. When the load is supplied from the AC input power source through the bypass switch, the AC supply terminals shall remain energized to permit operational checking of the system. Returning to normal mode shall be accomplished by placing the bypass switch in its normal position via the push-to-turn function, without disrupting power to the load.

    - Engineer’s Note: When specifying a wrap around maintenance bypass switch, select only (1) of the following two Maintenance Bypass options. If a wrap around maintenance bypass switch option is specified, the Internal Bypass Switch is still provided.

Break-Before-Make, Wall Mounted Maintenance Bypass: On inverter systems where the nominal input and output voltages are the same, an external, wall mounted, push-to-turn, 4 pole, break-before-make, wrap around maintenance bypass switch shall be provided for field installation. When in bypass mode, the switch will bypass the inverter system and feed the load power directly from the AC input power source. The inverter system’s main input breaker, output breaker, and battery breaker may then be opened, allowing the inverter to be fully serviced, including the complete maintenance and replacement of circuit cards or components. The bypass switch shall have an auxiliary contact to indicate the position of the switch for remote monitoring purposes. The bypass switch shall be provided with a padlock attachment for lockout/tagout purposes during maintenance.

Make-Before-Break, Wall Mounted Maintenance Bypass: On inverter systems where the nominal input and output voltages are the same, an external, wall mounted, push-to-turn, 4 pole, make-before-break, wrap around maintenance bypass switch shall be provided for field installation. When in bypass mode, the switch will bypass the inverter system and feed the load power directly from the AC input power source. The inverter system’s main input breaker, output breaker, and battery breaker may then be opened, allowing the inverter to be fully serviced, including the complete maintenance and replacement of circuit cards or components. The bypass switch shall have an auxiliary contact to indicate the position of the switch for remote monitoring purposes. A second auxiliary contact shall be wired to the inverter and invoke the system’s static bypass before the switch is turned to the bypass position. The bypass switch shall be provided with a padlock attachment for lockout/tagout purposes during maintenance.

2.6         Output Power Rating

System Power Output Capability: The stored emergency power supply system output power rating shall be (10kW) (13kW) (14kW) (15kW) (16kW) (17kW) (20kW) (22kW) (24kW) (26kW) (28kW) (30kW) (32kW) (33kW).

2.7         Battery Backup Time

Battery Time Reserve Capacity: Battery shall be capable of producing emergency power for (_) (30) (60) (90) (120) (240) minutes at full rated watts.

2.8         Main Circuit Breakers

    - System Input Breaker Rating: The inverter input breaker shall be included and sized to accommodate full rated load, low line input, and maximum recharge current simultaneously. An LSI adjustable breaker shall be provided.  (See Engineer’s Reference at the end of this specification for input breaker ratings and note regarding LSI breakers)

    - System Output Breaker Rating: The inverter output breaker shall be included and sized to accommodate full rated load continuously (and monitored to indicate an “output circuit breaker open” condition). An LSI adjustable breaker shall be provided.  (See Engineer’s Reference at the end of this specification for output breaker ratings and note regarding LSI breakers)

2.9         Input Specifications

- Input Voltage: (208/120 VAC) (480/277 VAC) (600/347 VAC), three phase (wye), 60Hz.

- Input Voltage Operating Range:  +10% to -15% at full load without battery usage.

- Frequency Range:  57 hertz to 63 hertz.

- Power Factor:  Self-correcting to >0.98 (approaching unity).

- Input Current Harmonics:  <10% THD (total harmonic distortion) at 100% load.

- System AIC (Amperes Interrupting Current) Rating: (10kAIC) (65kAIC).

2.10       Output Specifications

- Output Voltage: (208/120 VAC) (480/277 VAC) (600/347 VAC), three phase (wye), 60Hz

- Sine Wave Voltage:  3% THD (total harmonic distortion) maximum with linear load.

- Frequency: 60 Hz, +/- 0.5 Hz under full load while in the battery operation mode.

- Voltage Regulation: +/-3% typical

- Phase (Angle) Imbalance: 120 +/- 0.5

- Transient Voltage Response:

- 100% load step: +/- 10% for 1 cycle, then +/-3% for 2-3 cycles maximum

- Loss or return of AC input power: +/-3% for 2-3 cycles maximum

- Manual transfer of 100% load: +/- 10% for 1 cycle, then +/-3% for 2-3 cycles maximum

- Transient Voltage Recovery Time: 1 cycle to within 3% of nominal output voltage.

- Output Power Rating: KVA at 1.0 power factor (unity). KVA = KW

- Load Power Factor Range Permitted: 0.7 leading to 0.7 lagging (not exceeding full kVA/KW output rating).

- Overload Rating (without use of static bypass): Up to: 110% for 2 minutes, 125% for 30 seconds, 150% for 10 seconds, 400% for 4 cycles when fed from the AC power source, or on battery.

- LED Inrush Rating (without use of static bypass):  Peak overload capability of 1700% during a current surge of       ¼ cycle, when fed from the AC power source or on battery, to accommodate inrush current from LED fixtures/drivers.

- Fault Clearing (with bypass available): 150% for 1 minute, 500% for 1 second, 1000% for 1 cycle.

- Efficiency: 90% typical, kW and model dependent.

2.11	Battery Specifications

- Battery time:

(90 Minutes at full rated kilowatt output, listed ANSI/UL 924 Emergency Lighting and Power Equipment.)

(15)(30)(60)(120)(240) Minutes at full rated kilowatt output, listed UL 924 Auxiliary Lighting and Power Equipment.)

(30 Minutes at full rated kilowatt output, listed C-UL to CSA C22.2, No. 141-15 Emergency Lighting Equipment.)  Engineer’s Note: Consult factory for other C-UL listed battery run time.

- Battery Type:  Integral, valve regulated, sealed lead calcium, maintenance free, with front access terminals for ease of installation and maintenance.

- Charger:  3 stage, temperature compensated, smart charge.

- Recharge Time:  UL 924, NFPA 101, NFPA 111, and C22.2 No. 141-15 compliant.

- Bus Voltage:  Factory-programmable from 216 - 384 VDC, or from 132 - 168 VDC, kW rating and model dependent.

2.12       Environmental Specifications

- Operating Temperature:

(20°C to 35°C for ANSI/UL 924 Emergency Lighting and Power Equipment listed 90 minute models.)

(20°C to 35°C for UL 924 Auxiliary Lighting and Power Equipment listed (15)(30)(60)(120)(240) minute models.)

(10°C) or ( 20°C) to 35°C for 30 minute models C-UL listed to CSA C22.2, No. 141-15, Emergency Lighting Equipment.)

To satisfy (ANSI/UL 924 requirements for a 35°C listing)(C-UL / CSA requirements), (UL)(C-UL) testing shall have been performed in a 40°C environment, with the inverter system tested under full load and at low line input voltage. Optimum battery performance and life shall be achieved at 25°C.

- Inverter Storage Temperature:  -20°C to 50°C.

- Battery Storage Temperature:  25°C for 6 months before charging is required. For each 9°C rise, reduce storage time by half.

- Relative Humidity:  95% non-condensing.

- Elevation:  0 to 6600 ft. (2000 meters). Units installed at elevations greater than 6600 ft. shall be de-rated.

- Audible Noise Level: Not greater than 60 dba at 1 meter.

2.13	 Mechanical

    - Cabinet Dimensions for ANSI/UL 924 Emergency Lighting and Power Equipment listed models with 90 Minutes: (52”W x 33”D x 77”H) (63”W x 33”D x 77”H) (70”W x 33”D x 77”H)

Or specify

(for C-UL Listed models with 30 Minutes: (52”W x 33”D x 77”H) (63”W x 33”D x 77”H) (70”W x 33”D x 77”H)

Engineer’s Reference:

ANSI/UL 924 Listed models with 90 Minutes:

10kW – 14kW (208/120 VAC input and output):  52”W x 33”D x 77”H

10kW – 14kW (all other voltage configurations):  63”W x 33”D x 77”H

15kW – 17kW:  63”W x 33”D x 77”H

20kW – 22kW:  70”W x 33”D x 77”H

24kW:  63”W x 33”D x 77”H

26kW (480/277 VAC output):  63”W x 33”D x 77”H

26kW (208/120 VAC output):  70”W x 33”D x 77”H

28kW – 33kW:  70”W x 33”D x 77”H

C-UL Listed models with 30 Minutes:

10kW – 14kW (208/120 VAC input and output):  52”W x 33”D x 77”H

10kW – 14kW (all other voltage configurations):  63”W x 33”D x 77”H

15kW – 24kW:  63”W x 33”D x 77”H

26kW – 33kW:  70”W x 33”D x 77”H

NOTE: Add 14” to width if optional output distribution cabinet is specified to accommodate branch circuit breakers and/or a normally off output bus. Contact the factory for cabinet dimensions using other battery run times.

    - Enclosure: NEMA 1, powder-coat painted steel construction, and sealed prohibiting rodent entry.

    - Drip Shield:  A drip shield assembly shall be included to cover the inverter and battery cabinets (, and the output distribution cabinet). The assembly shall extend 2 inches beyond the inverter system cabinetry width and depth, and shipped loose for field installation.

2.14	 Display Monitor and Diagnostics

    - Display Monitor: An advanced display monitor shall be included to uphold NFPA and CSA guidelines for emergency illumination, emergency backup time, and unattended periodic and annual testing of the centralized emergency power system. The system shall include a local, front mounted, sealed, touch screen, color LCD display monitor to verify system electrical and temperature measurements, inform/alarm for abnormal system status, allow programming of user specified set points and inform of periodic system and battery test results.

    - Electrical Parameters – The three phase monitor shall display the following electrical parameters:

Input Voltage L-N

Input Frequency

Input Current L-N

Input VA L-N

Input Watts L-N

Input Power Factor L-N

Input KVA Total

Input KW Total

Output Voltage L-N

Output Frequency

Output Current L-N

Output VA L-N

Output Watts L-N

Output Power Factor L-N

Output KVA Total

Output KW Total

Output Percent Load L-N (% KVA)

Output Percent Load Total (% KVA)

Battery Voltage

Battery Charge/Discharge Current

    - Alarm Conditions – The three phase monitor shall display the following status and alarm conditions:

Input Over Voltage L-N

Input Under Voltage L-N

Improper Phase Rotation

Input Frequency High

Input Frequency Low

Output Over Voltage L-N

Output Under Voltage L-N

Output VA L-N High (output overload)

Output VA L-N Low (user-programmable limit referenced during automatic battery test, to verify integrity                 of egress lighting)

Output Frequency High

Output Frequency Low

Battery Voltage High

Battery Voltage Low

Battery Charger Current High

System On Battery

Low Battery Warning

Low Battery Shutdown

Over-Temperature Shutdown

- Inductors (if static bypass source is not available)

- IGBT (if static bypass source is not available)

- Transformer

- SCR

Input Fuse Failure

DC Link Over Voltage

DC Link Under Voltage

DC Charger (Rectifier) Failure / DC Open

IGBT Fault

Output Circuit Breaker Open

REPO Shutdown

System in Static Bypass

Static Bypass Input Out of Range

Static Bypass Fault

Excessive Auto Retransfers Attempted

Manual Restart Required

Battery Test Fail

    - Operational Conditions – The three phase monitor shall display the following operational conditions:

System Normal

System Alarm

System Shutdown

Battery Time Remaining (expressed in minutes)

Battery Test In Process (including a “countdown” of time remaining in test)

Off Bus Connecting

Off Bus Returning

System in Manual Bypass

System in Static Bypass

    - System Control – The three phase monitor shall allow for the following system control via the touch screen display:

Start Up

Shutdown

    - User-programmable Set Points – The three phase monitor shall allow for the following user-programmable set points:

High/low alarm thresholds

Low output VA level referenced during periodic and annual battery testing to verify egress lighting integrity

Off bus transition delays

Periodic battery test duration with date and time in compliance with NFPA 101 and C22.2 No. 141-15

Annual battery test duration with date and time in compliance with NFPA 101 and C22.2 No. 141-15

    - Periodic Testing – The three phase monitor shall incorporate system diagnostics and provide for automatic and manual testing of the system/batteries as follows:

- Feature a factory-set 5 minute battery discharge test every 30 days or 90 days, and a user-programmable (enable/disable) annual battery discharge test, factory-set for (30) (60) (90) (120) (240) minutes. Dates and times of tests shall be user-programmable.

- Report the battery test results with a pass/fail indication, time and date stamped, via the local monitor panel and via (BACnet/IP) (BACnet MS/TP) (Ethernet TCP/IP) (MODBUS TCP) (MODBUS RS485).

- During the battery test, the monitor shall perform a user-programmable egress lighting integrity test. The egress lighting integrity test shall measure the KVA load on the output of the system, and if the output load falls below the customer defined value, the inverter shall provide an audible and visual alarm, thus indicating fixture maintenance or component replacement.

- A manual, proprietary password protected “Push to Test” feature shall be provided to initiate NFPA 101-compliant system test. An “Abort Test” feature shall be included.

    - Data-Logging – The three phase monitor shall provide the following data-logging:

- Maintain a historic log that sequentially records a minimum of 25 battery tests which indicate time, date and pass/fail results. The log shall be made available through the local monitor and via (BACnet/IP) (BACnet MS/TP) (Ethernet TCP/IP) (MODBUS TCP) (MODBUS RS485) communications.

- Maintain a historic log that sequentially records 50 of the most recent alarms, indicating the time and date of abnormal occurrences. The log shall be made available through the local monitor display and via (BACnet/IP) (BACnet MS/TP) (Ethernet TCP/IP) (MODBUS TCP) (MODBUS RS485) communications.

2.15	Communications Interface

- Computer Port: System shall include an RS232 serial communications port for authorized access to electrical parameters, system status, alarms, system set point programming, and the test and alarm logs. Factory authorized service engineer shall have access to password-protected factory settings and configurations.

- Status / Alarm Relay Contacts: System shall include isolated, potential free (Form C) relay contacts accessible via a terminal strip for customer’s hardwired connection to building monitoring and security systems. Contacts shall be rated for 1A at 120VAC / 2A at 28VDC. Status / alarm contacts shall include inverter on, on battery power, low battery, general alarm, battery test pass, battery test fail, output circuit breaker open, in bypass, and periodic or annual system test activated.

- Remote Emergency Power Off  (REPO) Interface: System shall be provided with an REPO interface for customer’s normally open relay contact, which shall shut down the inverter system when the relay contacts close.

- Remote Monitoring Communications: Systems shall include remote monitoring and reporting of electrical parameters, system status, alarms, event logs, and automatic battery pass / fail test results with time and date stamp via (BACnet/IP) (BACnet MS/TP) (Ethernet TCP/IP) (MODBUS TCP) (MODBUS RS485).

2.16	Accessories (Optional Equipment)

    - Output Distribution Cabinet: The system shall include a factory-installed, side-mounted output distribution cabinet as defined in section 2.2 B of this specification to accommodate (factory-installed output branch circuit breakers as specified) (and) (the standby, normally off AC output bus as specified in section 2.3 C of this specification).

    - Standby Emergency Operation: The system shall include a normally off AC output bus as defined in section 2.3 C of this specification.

    - Wall Mounted Maintenance Bypass: The system shall be provided with an external wrap around maintenance bypass for field installation as defined in section 2.5 B of this specification.

    - Status / Alarm Relay Contacts: System shall include isolated, potential free (Form C) relay contacts as defined in section 2.15 B of this specification.

    - Remote Emergency Power Off  (REPO) Interface: System shall be provided with a REPO interface as defined in section 2.15 C of this specification.

    - Remote Monitoring Communications: Systems shall include remote monitoring and reporting as defined in section 2.15 D of this specification.

    - Remote Annunciator Panel: The system shall be provided with a remote annunciator panel for remote status indication of inverter on, on battery power, low battery, general alarm, and test active. The annunciator panel shall be provided with an interface cable of (50) (100) (150) (200) feet to connect to the inverter’s status / alarm terminal strip.

    - External Load Control Relay: Provide (Quantity) UL 924 listed load control relays to shunt around local control devices (i.e. dimmer control, wall switch, occupancy sensor) powered from the inverter’s normally on output, in order to provide full illumination to designated emergency lights upon the failure or loss of commercial AC power.

    - External Zone Sensing: Provide (Quantity) UL 924 listed load control relay(s), (each) wired for zone sensing and control of normally off  (standby) emergency lighting fixtures. The relay shall sense the voltage at an individual zone lighting panel. When loss of normal power is detected, emergency power shall be made available to illuminate emergency fixtures within that specific zone.

    - Drip Shield:  A drip shield assembly shall be included to cover the inverter system cabinetry as defined in section 2.13C of this specification.

    - Monitored Inverter Output Breaker: The inverter’s main output circuit breaker shall be provided with an auxiliary contact to signal if the breaker is open. If opened or tripped, the system’s local monitor shall sound an alarm. (See *Engineer’s note below)

    - Branch Output Breakers: Include (quantity) pre-installed, (15) (20) (25) (30) amp, single pole, output circuit breakers for use with normally on AC output bus. (See *Engineer’s note below)

    - Branch Output Breakers: Include (quantity) pre-installed, (15) (20) (25) (30) amp, single pole, output circuit breakers for use with normally off AC output bus. (See *Engineer’s note below)

    - Branch Output Breakers: Include (quantity) pre-installed, (15) (20) (25) (30) amp, single pole, monitored output circuit breakers for use with normally on AC output bus. (See *Engineer’s note below)

    - Branch Output Breakers: Include (quantity) pre-installed, (15) (20) (25) (30) amp, single pole, monitored output circuit breakers for use with normally off AC output bus. (See *Engineer’s note below)

    - Branch Output Breakers: Include (quantity) pre-installed, (15) (20) (25) (30) (40) (50) (60) amp, (2 pole) (3 pole), output circuit breakers for use with normally on AC output bus. (See *Engineer’s note below)

    - Branch Output Breakers: Include (quantity) pre-installed, (15) (20) (25) (30) (40) (50) (60) amp, (2 pole) (3 pole), output circuit breakers for use with normally off AC output bus. (See *Engineer’s note below)

*Engineer’s Note:

The output distribution cabinet is capable of accommodating 1 pole, 2 pole, and 3 pole branch circuit breakers fed from an inverter system output of 208/120 VAC or 480/277 VAC. A total of 12 pole positions per phase (36 poles total) are available for unmonitored breakers, or a total of 8 pole positions per phase (24 poles total) are available for monitored breakers.

1 pole breakers are available at 15, 20, 25, and 30 amp ratings. 2 pole and 3 pole 208 VAC breakers are available at 15, 20, 25, 30, 40, 50, and 60 amp ratings. 2 pole and 3 pole 480 VAC breakers are available at 15, 20, 25, and 30 amp ratings.

Branch circuit breakers can be wired to the normally on AC output bus and/or normally off AC output bus in any combination.  If a monitored branch circuit breaker is open, the system’s local monitor will sound an alarm. If the Status / Alarm Relay Contacts Option is specified, “output circuit breaker open” form C alarm contacts are provided for remote monitoring.

If the inverter’s main output circuit breaker is monitored and open, the system’s local monitor will sound an alarm. If the Status / Alarm Relay Contacts Option is specified, “output circuit breaker open” form C alarm contacts are provided for remote monitoring.

2.17	Serviceability

The inverter’s power section, including all control cards and system electronics, shall be front-accessible and located behind a secure hinged access door for ease of service or component replacement. An internal inverter bypass switch must be provided. A DC circuit breaker and DC Anderson connector shall be incorporated into the design to facilitate rapid replacement of the batteries via the front of the system enclosure. No side access shall be required. To facilitate inverter diagnostics and programming, a RS232 serial communications port shall be provided for access to electrical measurements, system set points, and system logs.

2.18	Warranty

    - The manufacturer shall guarantee the inverter’s power components and system electronics to be free from defects in material and workmanship during the warranty period. Inverter systems shall include a factory-authorized start up service, after which a (2 year parts and first year) (2 year parts and 2 year) (3 year parts and 3 year) factory-authorized on-site labor warranty shall be provided.

    - Battery warranty shall be 1 year full replacement, 14 year prorated.

End of Guide Specification

(See Engineer’s Reference next pages)

Engineer’s Reference

- System Input / Output Circuit Breaker Ratings

| Unit kVA/kW | Input Voltage Rating | Input Circuit Breaker Ratings |  | Output Voltage Rating | Output Circuit Breaker Ratings |  |
| --- | --- | --- | --- | --- | --- | --- |
|  |  | Amps | Volts |  | Amps | Volts |
| 10 | 208 | 50 or 60 ¹ | 240 | 208 | 35 | 240 |
|  | 480 | 25 | 480 | 480 | 15 | 480 |
|  | 600 | 20 | 600 | 600 | 15 | 600 |
| 13 | 208 | 70 | 240 | 208 | 45 | 240 |
|  | 480 | 30 | 480 | 480 | 20 | 480 |
|  | 600 | 25 | 600 | 600 | 20 | 600 |
| 14 | 208 | 70 or 80 ² | 240 | 208 | 50 | 240 |
|  | 480 | 35 | 480 | 480 | 25 | 480 |
|  | 600 | 25 or 30 ³ | 600 | 600 | 20 | 600 |
| 15 | 208 | 80 | 240 | 208 | 60 | 240 |
|  | 480 | 35 | 480 | 480 | 25 | 480 |
|  | 600 | 30 | 600 | 600 | 20 | 600 |
| 16 | 208 | 90 | 240 | 208 | 60 | 240 |
|  | 480 | 35 or 40 4 | 480 | 480 | 25 | 480 |
|  | 600 | 30 | 600 | 600 | 20 | 600 |
| 17 | 208 | 90 | 240 | 208 | 60 | 240 |
|  | 480 | 40 | 480 | 480 | 25 | 480 |
|  | 600 | 30 or 35 5 | 600 | 600 | 20 | 600 |
| 20 | 208 | 110 | 240 | 208 | 70 | 240 |
|  | 480 | 50 | 480 | 480 | 30 | 480 |
|  | 600 | 40 | 600 | 600 | 25 | 600 |
| 22 | 208 | 125 | 240 | 208 | 80 | 240 |
|  | 480 | 50 | 480 | 480 | 35 | 480 |
|  | 600 | 40 | 600 | 600 | 30 | 600 |
| 24 | 208 | 125 or 150 6 | 240 | 208 | 90 | 240 |
|  | 480 | 60 | 480 | 480 | 40 | 480 |
|  | 600 | 50 | 600 | 600 | 30 | 600 |
| 26 | 208 | 150 | 240 | 208 | 100 | 240 |
|  | 480 | 60 | 480 | 480 | 40 | 480 |
|  | 600 | 50 | 600 | 600 | 35 | 600 |
| 28 | 208 | 150 | 240 | 208 | 100 | 240 |
|  | 480 | 60 or 70 7 | 480 | 480 | 50 | 480 |
|  | 600 | 50 or 60 8 | 600 | 600 | 35 | 600 |
| 30 | 208 | 175 | 240 | 208 | 110 | 240 |
|  | 480 | 70 | 480 | 480 | 50 | 480 |
|  | 600 | 60 | 600 | 600 | 40 | 600 |
| 32 | 208 | 175 | 240 | 208 | 125 | 240 |
|  | 480 | 70 | 480 | 480 | 50 | 480 |
|  | 600 | *60 | 600 | 600 | 40 | 600 |
| 33 | 208 | 175 | 240 | 208 | 125 | 240 |
|  | 480 | 70 or 80 9 | 480 | 480 | 50 | 480 |
|  | 600 | 60 | 600 | 600 | 40 | 600 |
| ¹ 50A breaker with 208/120 VAC output, 60A breaker for other output voltages ² 70A breaker with 208/120 VAC output, 80A breaker for other output voltages 3 25A breaker with 480/277 VAC output, 30A breaker for other output voltages 4 40A breaker with 208/120 VAC output, 35A breaker for other output voltages 5 30A breaker with 480/277 VAC output, 35A breaker for other output voltages 6 125A breaker with 480/277 VAC output, 150A breaker for other output voltages 7 60A breaker with 480/277 VAC output, 70A breaker for other output voltages 8 50A breaker with 480/277 VAC output, 60A breaker for other output voltages 9 70A breaker with 480/277 VAC output, 80A breaker for other output voltages Note: LSI main input and output breakers are standard when the output breaker is rated for 35A or less. LSI breakers are optional on all other models. |  |  |  |  |  |  |

- UL 924 Listed Models – Weights & BTUs

| UL 924 LISTED MODELS W/ 90 MINUTES |  |  |  |
| --- | --- | --- | --- |
| kVA / kW | INPUT - OUTPUT VAC | WEIGHTS (LBS) | BTU'S / HOUR FULL LOAD |
| 10 | 208/120 - 208/120 | 2840 | 3410 |
| 10 | 480/277 - 208/120 | 3708 | 4092 |
| 10 | 480/277 - 480/277 | 3120 | 3410 |
| 13 | 208/120 - 208/120 | 3200 | 4433 |
| 13 | 480/277 - 208/120 | 4068 | 5320 |
| 13 | 480/277 - 480/277 | 3642 | 4433 |
| 14 | 208/120 - 208/120 | 3350 | 4774 |
| 14 | 480/277 - 208/120 | 4306 | 5729 |
| 14 | 480/277 - 480/277 | 3880 | 4774 |
| 15 | 208/120 - 208/120 | 4634 | 7161 |
| 15 | 480/277 - 208/120 | 4416 | 6138 |
| 15 | 480/277 - 480/277 | 4118 | 5115 |
| 16 | 208/120 - 208/120 | 4634 | 7638 |
| 16 | 480/277 - 208/120 | 4416 | 6547 |
| 16 | 480/277 - 480/277 | 4118 | 5456 |
| 17 | 208/120 - 208/120 | 4872 | 8116 |
| 17 | 480/277 - 208/120 | 4654 | 6956 |
| 17 | 480/277 - 480/277 | 4356 | 5797 |
| 20 | 208/120 - 208/120 | 5702 | 9548 |
| 20 | 480/277 - 208/120 | 5368 | 8184 |
| 20 | 480/277 - 480/277 | 5032 | 6820 |
| 22 | 208/120 - 208/120 | 6178 | 10503 |
| 22 | 480/277 - 208/120 | 5844 | 9002 |
| 22 | 480/277 - 480/277 | 5270 | 7502 |
| 24 | 208/120 - 208/120 | 5970 | 11458 |
| 24 | 480/277 - 208/120 | 5636 | 9821 |
| 24 | 480/277 - 480/277 | 5000 | 8184 |
| 26 | 208/120 - 208/120 | 6359 | 12412 |
| 26 | 480/277 - 208/120 | 6026 | 10639 |
| 26 | 480/277 - 480/277 | 5300 | 8866 |
| 28 | 208/120 - 208/120 | 6359 | 13367 |
| 28 | 480/277 - 208/120 | 6026 | 11458 |
| 28 | 480/277 - 480/277 | 5600 | 9548 |
| 30 | 208/120 - 208/120 | 6659 | 14322 |
| 30 | 480/277 - 208/120 | 6326 | 12276 |
| 30 | 480/277 - 480/277 | 5900 | 10230 |
| 32 | 208/120 - 208/120 | 6959 | 15277 |
| 32 | 480/277 - 208/120 | 6626 | 13094 |
| 32 | 480/277 - 480/277 | 6200 | 10912 |
| 33 | 208/120 - 208/120 | 7259 | 15754 |
| 33 | 480/277 - 208/120 | 6926 | 13504 |
| 33 | 480/277 - 480/277 | 6200 | 11253 |

C-UL listed models w/ 30 minutes – next page

- C-UL Listed Models – Weights & BTU’s

| C-UL LISTED MODELS W/ 30 MINUTES |  |  |  |
| --- | --- | --- | --- |
| kVA / kW | INPUT - OUTPUT VAC | WEIGHTS (LBS) | BTU'S / HOUR FULL LOAD |
| 10 | 208/120 - 208/120 | 2291 | 3410 |
| 10 | 208/120 - 600/347 | 3389 | 4774 |
| 10 | 600/347 - 208/120 | 3474 | 4774 |
| 10 | 600/347 / 600/347 | 3294 | 4774 |
| 13 | 208/120 - 208/120 | 2453 | 4433 |
| 13 | 208/120 - 600/347 | 3389 | 6206 |
| 13 | 600/347 - 208/120 | 3474 | 6206 |
| 13 | 600/347 / 600/347 | 3294 | 6206 |
| 14 | 208/120 - 208/120 | 2534 | 4774 |
| 14 | 208/120 - 600/347 | 3389 | 6684 |
| 14 | 600/347 - 208/120 | 3474 | 6684 |
| 14 | 600/347 / 600/347 | 3294 | 6684 |
| 15 | 208/120 - 208/120 | 3636 | 7161 |
| 15 | 208/120 - 600/347 | 3551 | 7161 |
| 15 | 600/347 - 208/120 | 3636 | 7161 |
| 15 | 600/347 / 600/347 | 3456 | 7161 |
| 16 | 208/120 - 208/120 | 3636 | 7638 |
| 16 | 208/120 - 600/347 | 3551 | 7638 |
| 16 | 600/347 - 208/120 | 3636 | 7638 |
| 16 | 600/347 / 600/347 | 3456 | 7638 |
| 17 | 208/120 - 208/120 | 3636 | 8116 |
| 17 | 208/120 - 600/347 | 3551 | 8116 |
| 17 | 600/347 - 208/120 | 3636 | 8116 |
| 17 | 600/347 / 600/347 | 3456 | 8116 |
| 20 | 208/120 - 208/120 | 3790 | 9548 |
| 20 | 208/120 - 600/347 | 3651 | 9548 |
| 20 | 600/347 - 208/120 | 3596 | 9548 |
| 20 | 600/347 / 600/347 | 3548 | 9548 |
| 22 | 208/120 - 208/120 | 3952 | 10503 |
| 22 | 208/120 - 600/347 | 3813 | 10503 |
| 22 | 600/347 - 208/120 | 3758 | 10503 |
| 22 | 600/347 / 600/347 | 3710 | 10503 |
| 24 | 208/120 - 208/120 | 4114 | 11458 |
| 24 | 208/120 - 600/347 | 3975 | 11458 |
| 24 | 600/347 - 208/120 | 3920 | 11458 |
| 24 | 600/347 / 600/347 | 3872 | 11458 |
| 26 | 208/120 - 208/120 | 4565 | 12412 |
| 26 | 208/120 - 600/347 | 4420 | 12412 |
| 26 | 600/347 - 208/120 | 4432 | 12412 |
| 26 | 600/347 / 600/347 | 4268 | 12412 |
| 28 | 208/120 - 208/120 | 4727 | 13367 |
| 28 | 208/120 - 600/347 | 4582 | 13367 |
| 28 | 600/347 - 208/120 | 4594 | 13367 |
| 28 | 600/347 / 600/347 | 4448 | 13367 |
| 30 | 208/120 - 208/120 | 4889 | 14322 |
| 30 | 208/120 - 600/347 | 4744 | 14322 |
| 30 | 600/347 - 208/120 | 4756 | 14322 |
| 30 | 600/347 / 600/347 | 4610 | 14322 |
| 32 | 208/120 - 208/120 | 5051 | 15277 |
| 32 | 208/120 - 600/347 | 4906 | 15277 |
| 32 | 600/347 - 208/120 | 4918 | 15277 |
| 32 | 600/347 / 600/347 | 4772 | 15277 |
| 33 | 208/120 - 208/120 | 5051 | 15754 |
| 33 | 208/120 - 600/347 | 4906 | 15754 |
| 33 | 600/347 - 208/120 | 4918 | 15754 |
| 33 | 600/347 / 600/347 | 4772 | 15754 |