CONTROLLED POWER COMPANY

MODEL LT	 - GUIDE SPECIFICATION

700 VA THRU 2.1 kVA SINGLE PHASE

UNINTERRUPTIBLE POWER SYSTEM

1.0	SCOPE

The Uninterruptible Power System (UPS) shall be an expandable single phase, continuous duty, line interactive, single conversion UPS designed to supply reliable, clean regulated power for critical loads.  The design shall incorporate an efficient ferro-resonant transformer, micro-processor controller, solid state PWM inverter and long lasting battery pack that provides immunity to all power line disturbances and power interruptions with no break in AC output power.

The synchronous inverter shall produce a true uninterrupted output in any mode of operation.   A self diagnostic monitoring alarm system that continuously advises system status shall be provided.

2.0	INDUSTRY STANDARDS

The following standards shall apply:

2.1	UL Listed 1778 Standards for UPS.

2.2	CSA Certified.

2.3	FCC Article 15, Section J, Class A.  Means it will not interfere with any other

electronic device, including computers and phones.

  - IEEE 587 category B guide for surge suppression.

2.5	ANSI/IEEE C62.41 and .45 category A and B.

2.6	IEC555 Power Factor specifications.

2.7	CBEMA and ANSI C84.1.  Must exceed the specifications and recommendations.

3.0	INPUT SPECIFICATIONS

3.1	INPUT VOLTAGE

120  208  240 VAC ,60 Hz.

220 VAC,  50 Hz.

3.2	OPERATING RANGE

+10% to -15% at full load.

3.3	KVA RATING

700 VA expandable to 850 VA

850 VA

1000 VA

1200 VA expandable to 1400 VA

1200 VA expandable to 1600 VA

1400 VA expandable to 1600 VA

1600 VA

1800 VA expandable to 2100 VA

2100 VA

3.4	FREQUENCY RANGE

Must capture 57.5 Hz to 62.5 Hz.

3.5	POWER FACTOR

Must be self correcting to >0.95 (approaching unity).

3.6	INPUT HARMONICS

<5% THD (total harmonic distortion).

3.7	ATTENUATION

Spike attenuation shall be a minimum of 3000:1.

4.0	FUZZY RANGE CONTROL

The UPS shall utilize a Fuzzy Range Control that allows a wider range of input voltage

variation (up to +10% to -40%) of nominal as an inverse function of load.  i.e. As the load

decreases the input band grows wider and more usable while maintaining the output

voltage at usable levels.  Operationally this means the unit must not use battery power

during simple brownout conditions, conserving the batteries for severe power 	outages.

4.1	FUZZY RANGING

The input range switch points must be infinitely variable as the load decreases.

Input band with 25% load shall be +10% to -40% with an output regulation of +4%.

Input band with 50% load shall be +10% to -30% with an output regulation of +4%.

Input band with 75% load shall be +10% to -20% with an output regulation of +4%.

5.0	OUTPUT SPECIFICATIONS

5.1	OUTPUT VOLTAGE

120 VAC, 60 Hertz

120/208 VAC, 60 Hertz

120/208 VAC, 60 Hertz

220 VAC, 50 Hertz

5.0	OUTPUT SPECIFICATIONS (continued)

Must provide a Sine Wave Voltage with maximum 3% harmonic distortion for any 					single harmonic not to exceed maximum 5% THD.  The output shall be rated for 					computer type loads with switch mode power supplies.

5.1	CREST FACTOR

Minimum 3 : 1.

5.2	K FACTOR

Must be rated K-30 or better.

5.3	POWER FACTOR

0.7 switch mode rated.

5.4	HARMONIC ATTENUATION

Load generated harmonics shall be attenuated 400% at the input.

5.5	LINE REGULATION

Better than +3%.

5.6	LOAD REGULATION

Better than +3%.

6.0	RESERVED

7.0	BATTERY

7.1	Run times shall be made available from 10 minutes to 72 hours.

7.2	BATTERY TYPE

Must be sealed, maintenance free, gas recombinant, self venting, suspended

electrolyte with no gel contaminant.  Batteries must be factory tested with specific 					inverter.

7.3 	BATTERY CHARGER

3 amp, two stage, not to exceed 25% of the amp hour rating.

7.4	RECHARGE TIME

3 hours to full charge.

7.5	BUSS VOLTAGE

Float 2.27 VPC, final 1.75 VPC.

7.6	LIFE

Batteries must have a Projected Life of 5 years service.

7.7	CAPACITY

The batteries shall be sized with the inverter to support the load at rated kVA with

a 0.7 power factor.

8.0	PERFORMANCE

8.1	OVERLOAD CAPABILTY

125% for ten minutes.

8.2	SURGE CAPABILITY

150% of rated output without need of static bypass.

8.3	FREQUENCY STABILITY

+0.2 Hz.

8.4	INNER WINDING CAPACITANCE

.01 pF (primary to secondary coupling).

8.5	COMMON MODE NOISE ATTENUATION

Must be 120 dB or greater (106 : 1 ground noise attenuation).

8.6	TRANSVERSE MODE NOISE ATTENUATION

Must be 70 dB or greater (3160 : 1 line noise attenuation),

(-3 dB at 1 kHz, -20 dB per decade).

8.7	REACTIVE POWER CORRECTION

Load at .6 pF must be corrected to >0.95 at input.

(automatically self correcting).

9.0	DIMENSIONS

Maximum Cabinet Dimension shall be 8.125"W x 17.5"D x 17.5"H

10.0  	DISPLAY MONITORS AND DIAGNOSTICS

10.1	Digital, 3 digit, bright LED Display shall be provided to display the following 					system parameters:

Input Voltage					Percent of Battery Capacity

Output Voltage					Percent of Battery Charger

Percent of Load

10.2	LED indicator lights shall be  provided to indicate the following system status:

System On (Green)				System On Battery (Yellow)

Low Battery Warning (Red)

10.3	LED indicator lights shall be  provided to indicate the following system Alarms 					(Red)

Low output					High output

Overload					Frequency fault

Over temperature				Shorted SCR shutdown

Low battery shutdown				Check battery

Output shutdown				Inverter on

Low battery					Remote/emergency power off shutdown

10.4	AUDIBLE ALARM

A switch selectable audible alarm shall be furnished

11.0	COMMUNICATIONS INTERFACE

11.1	STATUS AND ALARM PORT

A status and alarm port shall be furnished for network protection and unattended,

automatic shutdown for most LAN/WAN systems with optional Dataguard Advanced Software and NetcomTH SNMP adapter.

11.2	SERIAL PORT

A full duplex ASCII, RS/232 Serial Port shall be provided for over 60 operating,

diagnostic and performance characteristics.

12.0	ENVIRONMENTAL

12.1	ISOLATION

Isolation: shall be per NEC article 250-5d, and comply with this standard that

specifies a separately derived power source.

12.2	OPERATING TEMPERATURE

Operating Temperature is   0°C (32°F) to 40°C (105°F) without derating

12.3	STORAGE

Storage Temperature shall be 20° to 50° C.

12.4	HUMIDITY

Relative humidity 95% non condensed.

12.5	ELEVATION

5,000 feet, 1,500 meters.

13.0	MTBF

13.1	SYSTEM

Total System MTBF shall be a minimum of 100,000 hours

13.2	TRANSFORMER

The Transformer MTBF shall be a minimum or 200,000 hours.

13.3	MTTR

The Mean Time to Repair shall be less than one hour.

14.0	POWER DISTRIBUTION

14.1	The UPS shall have an efficient, flexible method of distributing power to this equipment, without going through expensive, time consuming, permanent wiring changes,

14.2	Provisions for three output configurations including the appropriately sized branch circuit breakers shall be provided:

14.2.1	FLUSH RECEPTACLE INTERFACE

The back panel must accommodate the specified NEMA standard receptacle(s).

14.2.2	FLEXIBLE EXTENSION WITH RECEPTACLE TERMINATION

The back panel shall be accommodate the specified flexible extension with 			specified receptacle termination.

14.2.3	FIELD WIRED TERMINATION

Hardwired provisions shall be furnished

15.0	WARRANTY

15.1	The manufacturer shall guarantee all systems to be free from material defects and workmanship for a period of 1 year following shipment from the factory.

15.2	Batteries shall be warranted with a 1 year full replacement warranty and an optional 4 year pro-rate with applicable maintenance contract.