CONTROLLED POWER COMPANY

GUIDE SPECIFICATIONS

FOR THE POWER PROCESSOR

SERIES 700A - POWER LINE CONDITIONERS

(Optional Items in Red)

1.0	GENERAL

This specification covers the electrical aspects for an AC Power Line Conditioner that shall provide clean regulated power to computers and other sensitive electronic equipment.  The system shall consist of an all copper, multiple tapped, triple shielded isolation transformer.  The transformer shall have a low impedance value to minimize voltage distortion.  The system shall contain independently controlled inverse parallel electronic switches for each of the 7 taps per phase to provide tight voltage regulation.  Linear devices shall be used for line synchronization to prevent phase shift errors normally associated with simple CT zero current crossing acquisition.  The system shall be microprocessor controlled.

The AC Power Line Conditioner is to be Controlled Power Company Series 700A - Power Processor or Owners / Engineers approved equal.

2.0	STANDARDS

All units shall be manufactured in accordance with the most recent editions of the following codes and standards:

- Institute of Electrical and Electronic Engineers (IEEE C62.41 - 1991 and IEEE 519-1992)

- National Fire Protection Association (NFPA) 70, National Electric Code (NEC)

- American National Standards Institute (ANSI C57.110)

- Federal Information Processing Standards Publication 94 (FIPS Pub 94)

- FCC Article 15, Section J, Class A

- Underwriters Laboratory (UL 1012)

2.1    LISTINGS

-     The system shall be listed to UL 1012 and CUL.

3.0	ENVIRONMENT

3.1	TEMPERATURE

The system shall be required to operate without overheating in an ambient 	temperature range of 0 C to 40 C.

3.2	HUMIDITY

Relative humidity of 0 to 95% non-condensing.

3.3	ALTITUDE

Sea level to 5000 feet above sea level.

3.4	AUDIBLE NOISE

Maximum allowable noise level shall not exceed 55dB when measured at 1 meter from the unit.

4.0	ELECTRICAL CHARACTERISTICS

4.1  INPUT POWER

4.1.1	The nominal AC input voltage rating of the system shall be ___________VAC, 			single phase, 60 Hertz; or ___________VAC, three phase delta derived, 60 			Hertz.

4.1.2	A molded case, manually operated, thermal magnetic, input circuit breaker 				(including input terminals) shall be provided.

4.1.3	A grounding terminal shall be provided for one parity sized grounding 				conductor.

4.2 OUTPUT POWER

4.2.1	The AC Power Line Conditioner continuous duty output power rating 				requirement is ________ KVA / KW, rated at unity power factor.

4.2.2	The output voltage of the system shall be __________ VAC, single phase, 60 			Hertz; or __________ VAC, three phase wye derived, 60 Hertz.

4.2.3	A newly derived neutral conductor shall be effectively bonded to the cabinet 			enclosure and a grounding terminal so that the isolated and conditioned 				output can be effectively referenced (grounded).

4.3	PERFORMANCE SPECIFICATIONS

4.3.1	Line Voltage Regulation - The AC power line conditioner shall provide an 			output voltage within + 3% of nominal when the input voltage is between 			+10%, -20% of nominal.  Optional extended range for intermittent duty shall 		provide an output voltage within +5%, -6% of nominal when the input voltage is 		between +10%, -40% of nominal.

4.3.2	Response Time - Response time shall be 1/2 cycle or less.

4.3.3	Correction Time - The output voltage shall be corrected within 1 cycle.

4.3.4	Circuitry - The regulator circuitry shall analyze the average voltage value of 			the AC power source to determine the correct tap.  A voltage source 			containing harmonics or a voltage waveform THD of <10% shall not effect 			output regulation parameters.

4.3.5	Output Impedance - The output impedance shall be typically 3%.

4.3.6	Load Regulation - The output shall be maintained to within 2.5% of nominal  		from no load to full load.

4.3.7	Operating Frequency shall be 60 Hertz + 3 Hertz

4.3.8	Harmonic Distortion - Less than 1% THD shall be added to the output 			waveform under any dynamic linear loading conditions.

4.3.9	Turn-On Characteristics - When energized the voltage overshoot shall be 5% 		or less of the nominal voltage for 1 cycle or less.

4.3.10	Overload Rating - The overload rating for the power conditioner shall be no 		less than 200% for ten seconds and 1000% for one cycle.

4.3.11	Noise Attenuation - Common mode noise attenuation shall be 140 dB or 			greater.  	Transverse mode noise attenuation shall be 3 dB down at 1000 			Hertz and 40 dB down per decade to below 50 dB with a resistive load.

4.3.12	Efficiency - The AC Line Conditioner shall have an efficiency of 97% or greater.

5.0      MAIN TRANSFORMER

5.1	BASIC CONSTRUCTION

The transformer windings shall be of all copper conductor construction with separate primary and secondary isolated windings.

5.2	MAGNETICS

Grain oriented, M6 grade, stress relieved, silicon transformer steel shall be utilized for minimum losses and to provide maximum efficiency.  Flux density shall not exceed 15 k gauss.

5.3	INSULATION

200C Class N insulation shall be utilized throughout.

5.4	SHIELDING

The transformer shall have at least __3___ copper shields to minimize inner winding capacitance, transients and noise coupling between primary and secondary windings.

5.5	COOLING

The transformer shall be designed for natural convection cooling.

  - TEMPERATURE RISE

The temperature rise of the transformer shall be no greater than 115˚C.

6.0	MAIN INPUT BREAKER

A main input, molded case, thermal magnetic circuit breaker rated at 125 % of the full load input current shall be furnished as an integral part of the unit.

7.0	BY-PASS SWITCH (OPTIONAL)

A rotary bypass switch shall be as an integral component, which will bypass the regulator portion of the Power Conditioner.  The regulator can be either on line or bypassed with one turn of the switch.  When in the bypass mode, the shielded isolation transformer shall remain on-line to provide clean, isolated, spike-free power.

8.0	MONITORING (Three phase units only)

8.1	ALERT LIGHT

An indicator light shall be provided to indicate that the output has been disabled by one of the following conditions:

Transformer over-temperature 			 Over-voltage (Optional)

SCR thermal overload				 Under-voltage (Optional)

  - PHASE INDICATOR LIGHTS (3 phase units only)

3 color-coded indicator lights, one for each phase, shall be illuminated when normal output power is present on each phase. In the event that output power is lost on one or more of the phases, the corresponding light will shut off for that phase.

9.0	CABINET

9.1	TERMINATION

Termination shall be rear access with input and output connections made of copper stand off bus for units above 150kVA. For units 150kVA and below, termination shall be of the terminal strip type.

9.2	VENTILATION

Ventilation shall originate from the bottom of the cabinet and exhaust at the rear of the cabinet for units 150kVA and below. For units 225kVA and above, ventilation shall originate from the bottom of the cabinet and exhaust at the top.

9.3	MOBILITY

The power conditioner cabinets shall be equipped with fixed casters located so as not to exceed 600-lbs./sq. inch on any one caster for units 150kVA and below. For units above 150kVA casters shall be replaced with steel channels.

9.4	ACCESSIBILITY

The cabinet shall be constructed with lift off panels on top and one side of the unit for ease of access.

10.0	CONTROLS

The control portion of the cabinet containing the circuit boards and connection to the semi-	conductor devices shall be separate from the transformer and input / output termination.

11.0	WARRANTY

Standard commercial one year warranty.